Service Manual

INVERTER

CONTENTS

1.Range & Conditions	3

2. Control Specifications	4

3. Exploded view	13

4. Refrigerant Flow Diagram	17

5. Circuit Diagram	18

6. Troubleshooting	20

7. Checking Electrical Components	26

8. Error Codes	27

# 1.Range & Conditions

## Operating Range

| Operating Modes | Temperature | Indoor Temperature | Outdoor Temperature |
| --- | --- | --- | --- |
| Cooling | Max. | 32℃ DB/27℃ WB | 43℃ DB/26℃ WB |
|  | Min. | 21℃ DB/15℃ WB | 21℃ DB |
| Heating | Max. | 27℃ DB | 24℃ DB/18℃ WB |
|  | Min. | 20℃ DB | -5℃ DB/-6℃ WB |

## Operating Conditions

|  | Rated Operating Conditions |
| --- | --- |
|  | Indoor Temperature | Outdoor Temperature |
| Cooling | 27℃ DB/19℃ WB | 35℃ DB/24℃ WB |
| Heating | 20℃ | 7℃ DB/6℃ WB |
| Tubing Length (m) | 4.0 |
|  | Max. Operating Value |
|  | Indoor Temperature | Outdoor Temperature |
| Cooling | 32℃ DB/23℃ WB | 52℃ DB |
| Heating | 27℃ | 24℃ DB/18℃ WB |

DB: Dry-bulb temperature

WB: Wet-bulb temperature

# 2. Control Specifications

## 2.1 General introduction

The indoor fan motor uses PG；The compressor is 4 poles brushless motor which rotary speed can be adjusted within 25-100rps.The outdoor controller has IPM transducer which can control the compressor and PFC control circuit，and the power factor of complete unit reaches up to more than 95%.

The aim of controlling：Temperature difference between indoor temperature and set temperature. This unit has the following control:

2.1.1 Indoor fan motor controls（PG motor）

Fan speed：High,medium,low,gentle.

2.1.2 Outdoor fan motor (AC machine)

Fan speed：High,low.

2.1.3 Capacity control

Change the capacity of cooling and heating through changing the rotate speed of compressor. The transducer can convert the voltage AC220V into volts d.c. and control the power supply condition of compressor by IPM module.

2.1.4 Over current protection

Outdoor controller examines input current and the compressor begins to run after accepting the order from indoor unit. When the current value exceeds the prescribed value, the outdoor controller will decrease the rotate speed of compressor, in that case, compressor can run at the speed by the order from indoor unit within the range of the current value does not exceed the prescribed value.

2.1.5 High-loaded prevention（freeze-prevention）

Indoor heat exchanger examines the condensation temperature of refrigerant when the unit is in heating operation.（evaporate temperature of refrigerant when cooling and heating）.If the temperature exceeds the prescribed value,(or lower than the prescribed value），then decrease the rotary speed of compressor to make compressor runs at the speed within the prescribed temperature range in order to keep high pressure from excessive rising.（Or

keeping indoor heat exchanger from freezing.）

2.1.6 Blades control

Users can realize tridimensional airflow through controlling vertical blades.

Control the position of blades automatically according to operating condition. Press“vertical

airflow ”button to set the position of vertical blades freely. Electric control will store the position of blades when the current is switched on.

2.1.7 Power-failure automatic reset

## 2.2 Panel display

2.2.1. See Q model for the details of panel display.

2.2.2 Emergency Run button: The unit will be turned off when pressing this button when the unit is in operation；

The unit will be turned on and operates in Smart mode after pressing this button when the unit is in off status.

2.2.3 Press any key when the unit is in operation, the buzzer will give a buzz sound ; When the unit is in off status, press the button of “on/off”, “air refresh” or “smart”, the unit will be turned on with a buzz sound.

2.2.4 Please see the operating instructions for the usage of remote controller.

## 2.3 Blades Control

The blades range for vertical blades is from1-5 point position. Press “vertical airflow” button, the blades will swing according to “1-2-3-4-5-swing-1-… “.But sometimes the blades can not be controlled because the unit is in protect function.

2.3.1 Cooling, Dehumidification and Air refresh function:

The blades will swing circularly within the range of 1-4.

In cooling and dehumidification operation, louver blades can change the position automatically to prevent from dripping.

2.3.2 Heating:

The blades will swing circularly within the range of 2-5.

During the course of heating beginning or defrosting（namely when the unit is in the pause condition），the blades are in fixed position to avoid blowing cold airflow because of the too low temperature of indoor evaporator. Only when the temperature of evaporator is higher than 32℃，will the unit enter normal control.

## 2.4 Cooling

2.4.1 Indoor blower control:

The fan speed can be set as high, medium, low and auto level.

If changed to auto level, the indoor blower will choose the fan speed according to room temperature and set temperature.

2.4.2 Cooling capacity control:

Calculating the difference value between the temperature detected by indoor pipe temperature sensor and the prescribed indoor pipe value temperature to determine the correction of frequency command signal, correct the frequency command signal currently existing. When the indoor pipe temperature is lower than the prescribed indoor pipe value temperature, the unit will decreases the rotary speed of compressor.

2.4.3 Freeze-prevention control:

Pipe coil sensor detects the temperature of indoor heat exchanger. If the temperature is lower than the prescribed value, then the unit decreases the rotary speed of compressor to keep the indoor heat exchanger from freezing. If the temperature exceeds the lower limit value, then please stop decreasing frequency; If the temperature exceeds the upper limit value, then the unit will exists freeze-prevention protection. If the temperature is lower than certain prescribed value, the unit will stop.

2.4.4 Over current-prevention control

If the value of input current detected by outdoor current sensor is higher than the prescribed value, the rotary speed of compressor will be decreased and controlled in order to keep the current value not higher than the upper limit value；compressor will come to normal operation when the current value drops to the lower limit value；If current value is higher than the upper limit value, compressor will stop.

2.4.5 Cooling overload working

In cooling operation, if the temperature of outdoor heat exchanger is too high, the speed of compressor will be adjusted to a lower gear automatically ，and sometimes compressor may be stopped.

2.4.6 Sleep control（soft operation）

Press“sleep” button on remote controller，the unit will control rotary speed of compressor and indoor fan motor and enters sleep operation:

Rotary speed of fan motor：medium level or low level

Rotary speed of compressor：decrease

The set temperature will increase 1℃ automatically after running for 1 hour; After running for about 1 hour, the set temperature will increase 1℃ ；After running for another 1 hour, the set temperature will go on increasing 1℃. The temperature will not increase when the set temperature is higher than the prescribed value. The temperature will not exceeds the prescribed value when lower than the prescribed value.

2.4.7 The highest rotary speed of compressor controlled by wind rate grade

To determine the highest rotary speed of compressor according to indoor and outdoor

temperature.

2.4.8 Outdoor Motor Control

The speed of outdoor motor is decided in low or higher according to the outdoor surroundings temperature and the indoor pipe temperature.

2.4.9 Dry Mildew Proofing Operation

Indoor fan motor will go on running for a period of time after the unit is turned off

to dry surplus moisture remain in unit.

2.4.10 Compressor frequency control

A Frequency range of compressor is 25-100Hz。

B Original frequency of compressor：Set by original indoor temperature and surroundings

temperature.

C Running frequency of compressor is controlled by artificial intelligence.

## 2.5 Heating

2.5.1 Indoor fan motor control

Fan speed：High,medium,low,auto.

If choosing “Auto” mode, then indoor fan motor chooses fan speed according to indoor

temperature and the set temperature.

2.5.2 Cool-airflow-prevention while heating

Avoid cool airflow：At the beginning of heating mode, if the temperature of indoor pipe coil is lower than the prescribed value, and compressor stops or running time less than the prescribed time （ If exceeding the prescribed time,the unit will exist

cool-airflow-prevention.），the unit is in cool-airflow-prevention condition, then louver blades can not swing and indoor fan motor stops. The PAUSE indicator lights during cool-airflow-prevention period.

2.5.3 Heating capacity control

Calculating the difference value between the temperature detected by indoor pipe temperature sensor and the prescribed indoor pipe value temperature to determine the correction of frequency command signal, correct the frequency command signal currently existing. When the indoor pipe temperature is higher than the prescribed indoor pipe value temperature, the unit will decreases the rotary speed of compressor.

2.5.4 High-loaded control

Indoor pipe coil temperature sensor examines evaporator temperature, if temperature

exceeds the prescribed value, the frequency does not increase; if temperature exceeds upper limit value, the rotary speed of compressor will be gradually decreased to avoid too high heat load；if temperature is lower than the prescribed value, the frequency does not decrease; if temperature is lower than lower limit value, unit will exist high-loaded control and enters normal operation.

2.5.5 Over current control

If the value of input current detected by outdoor current sensor is higher than the prescribed value, the rotary speed of compressor will be decreased and controlled in order to keep the current value not higher than the upper limit value；compressor will come to normal operation when the current value drops to the lower limit value；If current value is higher than the prescribed value, compressor stops.

2.5.6 Defrosting control

2.5.6.1 Defrosting test

When machine is in heating mode, it controls defrosting through defrosting sensor (Te) detecting the frost level of heat exchanger.

2.5.6.1.1The first conditions of entering defrosting:

2.5.6.1.1.1 The prerequisite of defrosting: heating compressor is running for 10 minutes and 45 minutes in total ( general defrosting)/ 90 minutes 【（low temperature defrosting：outer environmental temperature is under －6℃】；

2.5.6.1.1.2 Sufficient conditions of entering defrosting as below:

2.5.6.1.1.2.1 Not to enter defrosting if outer environmental temperature is above 15℃;

2.5.6.1.1.2.2 Enter defrosting if outer environmental temperature is under -6℃and defrosting temperature is less or equal to -15℃ for 5 minutes;

2.5.6.1.1.2.3 Enter defrosting if outer environmental temperature is between 【5℃－15℃】 and defrosting temperature is less or equal to -6℃ for 5 minutes;

2.5.6.1.1.2.4 Enter defrosting if outer environmental temperature is between 【-6℃－5℃】 and defrosting temperature is less or equal to TeS for 5 minutes.

TeS=C*outer environmental temperature-A   A=8 Outer environmental temperature<0℃ C=0.8  outer environmental temperature >=0℃ C=0.6

2.5.6.1.2The second conditions of entering defrosting:

Compressor runs for 3 hours, but not to enter defrosting and temperature of condenser pipe is less -2℃ for 3 minutes

2.5.6.2 Defrosting operation

Stop compressor first and turn off 4-way valve relay and outdoor fan motor；Turn on compressor again. Outdoor fan stops while defrosting.

2.5.6.3 Existing defrosting

Defrosting operation will change into heating operation when meeting any of the following condition:

1）Outdoor heat exchange is higher than the prescribed value.

2）Outdoor heat exchange is higher than the prescribed value for a consecutive period of time.

3）Time of defrosting is longer than the longest time of prescribed time.

2.5.6.3 Defrosting note:

2.5.6.3.1 Machine will not stop when the compressor frequency doesn’t go up to 80Hz, switched to non-heating mode after entering defrosting.

2.5.6.3.2 Sensor error code will not be shown in the display of indoor during defrosting even if the sensor has problems, but the error code will be shown 3 minute after the compressor starts to run when the machine is restarted after defrosting exits, or the compressor will open or close according to the environmental temperature.

2.5.6.3.3 The outdoor unit will not detect the temperature of indoor sensor during defrosting.(The outdoor unit always detects the inner environmental temperature, but the detected result is no use for outdoor unit.)

2.5.6.3.4 The conditions of ending defrosting must be detected 2 minutes after the compressor starts to run.

2.5.6.3.5 Compressor running time record will not be refreshed if the machine is not switched to non-heating mode, even if the machine is turned off.

2.5.7 Blowing surplus energy function

When turning off compressor, indoor fan motor chooses low speed operation( gentle/stop) according to temperature of indoor pipe coil to make the best of surplus energy of indoor pipe coil.

2.5.8 Temperature control for compressor vent

Vent temperature sensor detects the temperature of refrigerant air exhausted from

compressor and control rotary speed of compressor（same as cooling and heating）to ensure high efficient operation of system.

2.5.9 Sleep control（soft operation）

Press“sleep” button on remote controller，the unit will control rotary speed of compressor and indoor fan motor and enters sleep operation:

Rotary speed of fan motor：medium level or lower lever

Rotary speed of compressor：decrease

The set temperature will decrease 1℃ automatically after running for 1 hour; After running for another 1 hour, the set temperature will go on decreasing 1℃. But the set temperature displayed on LED will remain unchanged.

2.5.10 Outdoor fan motor control（except defrosting）

The speed of outdoor motor is decided in low or higher according to the outdoor surroundings temperature and the indoor pipe temperature.

2.5.11 compressor frequency control

A Frequency range of compressor is 25-100Hz。

B Original frequency of compressor：Set by original indoor temperature and surroundings

temperature.

C Running frequency of compressor is controlled by artificial intelligence.

## 2.6 “Smart”function

The unit will judge the operation mode automatically after receiving the SMART signal.

2.6.1 Original set temperature：Choosing indoor temperature according to set temperature.

2.6.2 Original mode ： Choosing original mode according to outdoor temperature and indoor temperature. There are three modes are available: cooling, heating, fan sweep

Fan sweep mode：High level，louver blades swing automatically and can be adjustable.

In“Smart”mode, all additional function is available. Indoor fan speed is set as automatic and louver swing automatically. Outdoor rotary speed is controlled according to the corresponding mode, and users can adjust position of louver and temperature.

Unit will judge next working mode after finishing operation of a kind of mode. If in fan sweep mode, unit will enter mode to judge program every per minute until enter cooling or heating mode.

2.6.3 Judge mode again：Choosing cooling(heating/fan sweep) mode according to indoor, outdoor temperature and the set temperature.

## 2.7 Dehumidification

2.7.1 When indoor temperature is higher than a certain temperature value, and higher than(set temperature），unit operates in cooling mode and outdoor fan speed is the same with the speed in cooling operation；or unit operates in dehumidifying operation according to indoor temperature and outdoor fan motor is at low speed level.

When indoor temperature is higher than the upper limit value, compressor operates by a certain prescribed frequency.

When indoor temperature is between upper limit temperature and lower limit temperature，compressor operates by a prescribed frequency.

When indoor temperature is lower than lower limit temperature, compressor stops.

2.7.2 Fan motor runs at low speed level.

2.7.3 Freeze-prevention control: same as cooling mode.

2.7.4 Dry Mildew Proofing Operation: same as cooling mode.

## 2.8 Other functions

2.8.1 Timelag protection function for compressor

In order to protect compressor（expect for defrost mode）,there will be a 3-minute delay to restart when compressor stops from working condition. And there is still 3 minute delay when the compressor is firstly started.

2.8.2 Automatic restart

This function refers to：When the electricity comes again after power failure, the unit is required to get back to the condition before power failure automatically. The mode, set temperature, air refresh, sleep, lock for the safety of children, humidification and air ventilation all keep in the same condition before power failure.

This function can be set or cancelled through EEPROM device on electric board or the

installation of peripheral circuit.

2.8.3 Independent air refresh function

Press “air refresh”button on remote controller when the unit is in off status, the unit is in Fan Sweep mode. Press this button again, this function can be cancelled.

2.8.4.Timing on/off

1.  Turn on the air conditioner on timer: The air conditioner will starts operation at the set time.“time on”function is only effective for once in 24 hours. If user turns on the air condition by pressing on/off button on the remote controller before the set time, then” timing on” function will be cancelled. If user select “timing on” when the air conditioner is in on status, the air conditioner will stop immediately and restart automatically at set time.

2.  Timing off: The air conditioner will exit running at set time. ” timing off” function is only effective for once in 24 hours. If user turns off the air condition by pressing on/off button on the remote controller before the set time, then” timing on” function will be cancelled. If user selects “timing off” when the air conditioner is in off status, the air conditioner will run immediately and stop automatically at set time.

3.  Program timing control：Air conditioner is turned on/off automatically at set time every day. if user turn off the air conditioner by pressing off button before the set time, then the “timing off” function will be cancelled but the “timing on” function is still effective；If user turns off the air conditioner by pressing on the emergency button before the set time, then the program timing control will be cancelled. If user turn on the air conditioner by pressing on the on button on the remote controller before the set time, then timing on function will be cancelled but the timing off function is still effective; if the user turn of the air conditioner by pressing on emergency button before set time, then the program timing control will be cancelled.

2.8.5 Induction function(of remote controller)

The remote controller sends the room temperature signal to air conditioner once time in every 3 minutes, and the unit will run according the signal. To detect the room temperature, remote controller must be placed in the area where the signal of remote control can be received. If the signal from remote control can not be received in 5 minutes, the air conditioner will operate according to the temperature which detected by indoor temperature sensor.

2.5.10  UVC function（optional）

Press the UVC bottom on remote controller to start or stop UVC sterilize function.

Note：

1.This appliance contains a UVC lamp.

2.Unintended use of the appliance or damage to the housing may result in the escape of dangerous UVC radiation. UVC radiation may, even in small doses, cause harm to the eyes and skin.

3.Appliances that are obviously damaged must not be operated. Prior to cleaning or other maintenance, the appliance must be disconnected from the supply mains.

# 3. Exploded view

## 3.1 Exploded view for indoor unit

| NO. | Materails Description | NO. | Materails Description |
| --- | --- | --- | --- |
| 1 | Front panel subassembly | 22 | electric heating tube |
| 2 | Front panel | 23 | Positive and negative ion generate |
| 3 | Air filter | 24 | Sensor bracket |
| 4 | Medium frame subassembly | 25 | Electric control board |
| 5 | Screw cover | 26 | Spring |
| 6 | Evaporator subassembly | 27 | Display box |
| 7 | pressure plate | 28 | Display P.C.B assembly |
| 8 | Bearing | 29 | WIFI subassembly |
| 9 | Bottom frame subassembly | 30 | Electric control box board(metal) |
| 10 | Stepping motor | 31 | Cover of electirc control box |
| 11 | Blade | 32 | Transformer |
| 12 | Wall-Mounting frame | 33 | Terminal board |
| 13 | Pipe pressure plate | 34 | Wire pressure plate |
| 14 | Drainage pipe subassembly | 35 | Electirc control box |
| 15 | Stepping motor | 36 | P.C.B assembly |
| 16 | Crossflow fan | 37 | Electric control box(metal shell) |
| 17 | Motor Bracket (bottom) | 38 | Power line |
| 18 | Fan motor | 39 | Room temperature sensor |
| 19 | Motor Bracket（top) | 40 | Pipe temperature sensor |
| 20 | Motor cover | 41 | Negative ion generator |
| 21 | Negative ion generator |  |  |

NOTE:Actual product may be different from above graphics,please refer to actual products.

## 3.2 Exploded view for outdoor unit

| NO. | Enlish description |
| --- | --- |
| 1 | front net cover |
| 2 | front plate subassembly |
| 3 | propeller fan |
| 4 | fan motor |
| 5 | motor bracket subassembly |
| 6 | bottom plate subassembly |
| 7 | Metal support |
| 8 | partition board |
| 9 | Top cover assembly |
| 10 | condenser subassembly |
| 11 | rear net cover |
| 12 | Sensor holder |
| 13 | capillary subassembly |
| 14 | outdoor electric control subassembly |
| 15 | Platen |
| 16 | Terminal seat |
| 17 | Electrical inseallation board |
|  | Electrical inseallation board |
| 18 | reactor |
| 19 | electric cover subassembly |
| 20 | Valve mounting plate |
| 21 | Lateral plate assembly |
| 22 | cut-off valve 3/8 |
|  | cut-off valve 1/4 |
| 23 | four-way valve subassembly |
| 24 | compressor |

NOTE:Actual product may be different from above graphics,please refer to actual products.

# 4. Refrigerant Flow Diagram

###### Thermal insulating of refrigerant pipeline

To prevent heat loss and condensed water from dropping on the floor, the wide and narrow tube of air conditioner should be wrapped with thermal insulating materials. For using capillary tube, and the tubes are in low temperature, the thickness of thermal insulating materials shall be more than 8mm.

# 5. Circuit Diagram

## 5.1 Electrical wiring diagram for indoor unit

To avoid electrical shock hazard, be sure to disconnect power before checking, servicing and/or cleaning any electrical parts.

## 5.2

## Electrical wiring diagram for outdoor unit

To avoid electrical shock hazard, be sure to disconnect power before checking, servicing and/or cleaning any electrical parts.

# 6. Troubleshooting

## 6.1 Check before troubleshooting

Check power line

To check whether the power line is connected correctly according to the wiring diagram.

6.1.2 Check unit wiring

To check whether the inter-unit wires are connected correctly.

6.1.3 .Check power supply

To check whether the power supply is in the specified range (220±10%).

To check whether the power supply is being supplied.

6.1.4 Check connector and lead wire of indoor and outdoor units.

To check whether the insulating cover of the lead wire is damaged.

To check whether the lead wire and the connector are connected well

To check wires.

## 6.2 The air conditioner does not work

6.2.1 Leakage protector is open or fuse is burnt.

  - Setting leakage protector to “ON”, it opens immediately (can not reset).

There is possibility of ground fault.

Check insulation resistance (The insulation resistance shall be more than 2MΩ).

  - Leakage protector is OFF.

  - The fuse is open in several minutes after turning air conditioner on.

6.2.2 The indoor and outdoor units do not work.

6.2.3 Only outdoor unit does not work:

6.2.4 Only indoor unit does not work.

## 6.3 Some parts of the air conditioner do not work

6.3.1 Only indoor fan does not work.

6.3.2 Only louver motor does not run.

6.3.3 Only outdoor fan motor dos not run.

6.3.4 Compressor does not run.

## 6.4 Air conditioner operates, but abnormalities are observed

6.4.1 Bad shifting between cooling and heating mode

(Not available in cooling type).

Poor cooling or heating phenomena.

Note:           Only in heat pump air conditioner.

6.5 Over cooling or heating.

## 6.6 Sensor is defective

6.6.1 Temperature sensor of indoor heat exchanger is defective.

Definition of open or short circuit of sensor (thermal resistor):

Short circuit: The protective cover of a lead wire has been damaged, and the exposed wire is touching another metal parts. Or both lead wires have become exposed and are touching each other. Or the circuit inside the temperature sensor is closed.

Open: The lead wires are broken, or the circuit inside the temperature sensor is open.

# 7. Checking Electrical Components

## 7.1 Measure insulation resistance

The insulation is in good condition if the resistance exceeds 2 MΩ.

7.1.1 Power supply wires

Clamp the ground pins of the power plug with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on either of the power wires. (Fig. 1)

Then measure the resistance between the

ground wire and the other power wire. (Fig. 1)

7.1.2 Indoor unit

Clamp an aluminum plate fin or copper tube with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on each terminal screw on the terminal plate. (Fig. 2)

Note that the ground line terminal should be skipped for the check.

7.1.3 Outdoor unit

Clamp a metallic part of the unit with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on each terminal screw where power supply lines are connected on the terminal plate. (Fig. 2)

7.1.4 Measurement of Insulation Resistance for Electrical Parts

Disconnect the lead wires of the desired electric part from terminal plate. Capacitor, etc.

Similarly disconnect the connector. Then measure the insulation resistance. (Fig. 3 and 4)

## 7.2 Checking continuity of fuse on PCB ass”y

Remove the PCB ass’ y from the electrical component box. Then pull out the fuse from the PCB ass’ y. (Fig. 5)

Check for continuity using a multimeter as shown in Fig. 6

## 7.3 Checking motor capacitor

Remove the lead wires from the capacitor terminals, and then place a probe on the capacitor terminals as shown in Fig. 7. Observe the deflection of the pointer setting the resistance measuring range of the multimeter to the maximum value.

The capacitor is “good” if the pointer bounces to a great extent and then gradually returns to its original position.

The range of deflection and deflection time differ according to the capacity of the capacitor.

# 8.ERROR CODES

# Text boxes

###### Warning

###### Warning

High-voltage will result in electric shock or death.

Always cut off the power before checking and maintaining.

Warning:

Disconnect unit wires from terminal block of outdoor unit. And measure insulation resistance of outdoor unit.

Poor insulation performance

No

Measure the insulation resistance of the electric parts of outdoor unit.

Disconnect unit wires from terminal block of indoor unit. Unplug the unit and measure the insulation resistance of indoor unit.

No

Measure the insulation resistance of the electric parts of outdoor unit.

Poor insulation performance

Check the rated power of fuse.

Check the resistance of indoor fan motor coil.

Check the resistance of transformer coil.

Replace it with a proper one

Replace indoor fan motor.

Replace transformer.

No

No

No

Yes

Yes

Check power supply

Check if something residue cover on transmitting part of the remote controller.

1. Power failure

2. Check the breaker.

Clean it.

Check if infrared receiver on indoor unit is dirt.

Clean it.

Check fuse on indoor PCB Ass’ y.

Check the resistance of fan motor coil of indoor unit.

Parts of indoor PCB Ass’ y or switches are defective.

Measure the resistance of power transformer.

No

No

No

No

Yes

Yes

Yes

Yes

Check the set temperature.

1. The set temperature is too high for cooling operation.

2. It is too low for heating operation.

Adjust the set temperature.

Measure the voltage between terminal No.1 and No.2 on the terminal block (220V±10%)

PCB Ass’ y of indoor unit is defective.

Outdoor unit is defective.

Yes

Ok

No voltage indication.

Indoor PCB Ass’ y is defective.

Check the fan rotation

Check if foreign matter is in the fan cover.

Check if fan motor is broken or foreign matter in bearing.

Measure the resistance of motor coil.

Check the capacitor of fan motor.

Ok

Ok

Not rotate

Measure the resistance of the louver motor coil.

Check the connector.

Check the fan rotation

Check if foreign matter is in the fan cover.

Check if fan motor is broken or foreign matter in bearing.

Measure the resistance of motor coil.

Check the capacitor of the fan motor.

Ok

Ok

Not rotate

Check compressor capacitor.

Measure the resistance of compressor coil.

Measure the resistance of   power relay coil.

Measure if power supply voltage is too low.

Overload protector activates.

The temperature of compressor is too high.

Refrigerant is not enough.

Fill it.

Rotor may be blocked.

Yes

No

Remote controller may be detective.

Measure the coil resistance of 4-way reversing valve.

Cooling

Heating

Measure the voltage between terminal No.5 and No.2 on the terminal block (ov).

NO voltage

PCB Ass’ y of indoor unit is in error.

4-way reversing valve is defective.

Ok

Check the voltage between terminal No.5 and N0.2 on the terminal block (AC220)

Cooling

Heating

Poor cooling (heating) performance

Is the temperature set properly?

Change the set temperature.

The heating (cooling) load is too large.

Reduce heat (cool) source or change the air conditioner with large power.

Refrigerant flow is not enough

Refrigerant is not enough.

Filling it

Capillary tube is blocked.

Replace it.

Compressor is in error.

Replace it.

Service valve is not open completely.

Open it completely.

Air circulating capacity is not enough.

The air filter is blocked.

Clean it.

4-way reversing valve fails.

Replace it

Fan running speed is at “low”.

Change it to “high’ or “medium”.

Connection between indoor and outdoor units is in poor thermal-insulated.

Wide and narrow tubes are thermal-insulated separately.

Cooling air -flow

4-way reversing valve is defective.

Replace it

Cooling airflow protector is no use.

The pause indicator is on.

Replace the electric controller of indoor unit.

Temperature sensor of indoor coil is defective.

Replace the sensor.

Check the set temperature.

The sensor is open or short.

The timer of indoor unit is flash.

Replace it.

Refer to electric wiring diagram.

If the probe can’ t enter the poles because the hole is too narrow then use a probe with a thinner pin.

Note: