Service Manual

ON-OFF

CONTENTS

1.Range & Conditions	3

2. Control Specifications	4

3. Exploded view	10

5. Refrigerant Flow Diagram	14

6. Circuit Diagram	15

7. Troubleshooting	18

8. Checking Electrical Components	24

9. Error Codes	25

# 1.Range & Conditions

## 1.1 Operating Range

| Operating Modes | Temperature | Indoor Temperature | Outdoor Temperature |
| --- | --- | --- | --- |
| Cooling | Max. | 32℃ DB/27℃ WB | 43℃ DB/26℃ WB |
|  | Min. | 21℃ DB/15℃ WB | 21℃ DB |
| Heating | Max. | 27℃ DB | 24℃ DB/18℃ WB |
|  | Min. | 20℃ DB | -5℃ DB/-6℃ WB |

## 1.2 Operating Conditions

|  | Rated Operating Conditions |
| --- | --- |
|  | Indoor Temperature | Outdoor Temperature |
| Cooling | 27℃ DB/19℃ WB | 35℃ DB/24℃ WB |
| Tubing Length (m) | 3 |
|  | Max. Operating Value |
|  | Indoor Temperature | Outdoor Temperature |
| Cooling | 32℃ DB/23℃ WB | 43℃ DB |
| Tubing Length (m) | 3 |

DB: Dry-bulb temperature

WB: Wet-bulb temperature

# 2. Control Specifications

## 2.1 System source

2.1.1 Signal input

Temperature sensor signal (indoor temperature , indoor coiled temperature, outdoor coiled temperature); remote control signal; key input.

2.1.2 Signal output

LED×4 (SI, SCK, RCK or air refresh, operation, pause, timer); louver motor (a, b, c, d); buzzer, compressor, 4-way reversing valve, indoor fan motor (H,L), outdoor fan motor, AUH, air refresh, and other assistant functions.

## 2.2 Control functions

2.2.1 Switches input:

Press the Emergency button on the panel when the air conditioner is in the off mode, then the unit will be turned on and work in the “SMART” mode. Press this button again when the unit is running (including test run or in “SMART” mode), the air conditioner will be turned off.

Note:

All the displaying will disappear when turn off the air conditioner by pressing the Emergency button.

2.2.2 Timer

Timing on/off

1.  Turn on the air conditioner on timer: The air conditioner will starts operation at the set time. “ time on”function is only effective for once in 24 hours. If user turns on the air condition by pressing on/off button on the remote controller before the set time, then” timing on” function will be cancelled. If user select “timing on” when the air conditioner is in on status, the air conditioner will stop immediately and restart automatically at set time.

2.  Timing off: The air conditioner will exit running at set time. ” timing off” function is only effective for once in 24 hours. If user turns off the air condition by pressing on/off button on the remote controller before the set time, then” timing on” function will be cancelled. If user selects “timing off” when the air conditioner is in off status, the air conditioner will run immediately and stop automatically at set time.

3.  Program timing control：Air conditioner is turned on/off automatically at set time every day. if user turn off the air conditioner by pressing off button before the set time, then the “timing off” function will be cancelled but the “timing on” function is still effective；If user turns off the air conditioner by pressing on the emergency button before the set time, then the program timing control will be cancelled. If user turn on the air conditioner by pressing on the on button on the remote controller before the set time, then timing on function will be cancelled but the timing off function is still effective; if the user turn of the air conditioner by pressing on emergency button before set time, then the program timing control will be cancelled.

3.2.3 Sleep mode:

When the sleep mode is set by remote, the set temperature will increase 1℃ after running 1 hour in cooling or Dehumidifying mode.  （Note：Display set temperature is unaltered）

When the air conditioner runs in sleep mode, the Max. indoor fan speed is set at medium level.

Note: The fan speed is set to be at low level, but the fan speed will turn into medium level when in freeze-prevention mode.

2.2.4 Unit type and Power

Please refer to PIN function

Note: After changing the unit type, the new unit type should be tested for the relevant function and protection differently according to different unit types.

2.2.5 Operation for dryness enzyme-prevention

When the unit is turned off in cooling mode, the indoor unit will continue run in low fan speed for about 3 minutes to remove the partial moisture in the room.

## 2.3 Auto-operating Mode

2.3.1 Auto-operating

The unit will judge the operation mode automatically after receiving the Auto signal.

2.3.1.1 After a/c entering auto-operating mode, the unit will run in auto mode. After starting auto mode, the sweeping indicator flashes ( on for 1.5 seconds and out for 0.5 seconds), indoor unit will be switched off and the outdoor unit will run at low fan speed level. The system will choose operation mode according to the present ambient temperature after 20 seconds:

when Tr≤20℃，fan only operates

when 20℃＜Tr＜24℃，dehumidification operates

when Tr≥24℃，cooling operates

2.3.1.2 The fan speed is at auto mode and adjustable, the display will change accordingly.

Note: If choosing the airflow mode, the auto airflow is set to be at low level automatically.

2.3.1.3 The airflow direction is swing and adjustable, and the display will change accordingly.

2.3.1.4 All output (air refresh,, air ventilate, etc.) is effective.

2.3.1.5 In cooling mode, the original set temperature is Ts=Tr-5℃ and 22℃≤Ts≤27℃, then the master unit will not change operation mode when the unit enters cooling mode.

If users want to change working condition by remote controller, in case the condition will not conflict with the master unit mode, ( such as cooling mode conflicts with AUH mode), the master unit will operate and display in new condition set by remote controller.

2.3.1.6 If users want to change working condition by remote controller, in case the condition will not conflict with the master unit mode, the master unit will operate and display in new condition set by remote controller.

2.3.2 Cooling:

Temperature control range: 16℃-32℃; Original value: 24℃;

Temperature control precision: ±1℃;

Characters on control:

4-way reversing valve closes:

When Tr≥Ts+1℃, compressor runs; When Tr≤Ts-1℃, compressor stops; The control circuit will stop compressor only after it has run at least 5 minutes. The compressor can be restarted 3 minutes later the turn-off.

Fan speed control:

Auto: When Tr>Ts+2℃, high speed;

When Ts< Tr≤Ts+2℃, medium speed;

When Tr≤T, low speed.

Manual: Users can select the fan speed of high, medium or low level as needed when the air conditioner is in the turn-on status.

Louver adjustment:

Manual (vertical direction): Set the blades position as needed.

2.3.3. Dehumidification:

Temperature control range: 16℃-32℃; Temperature control precision: ±1℃;

Characters on control:

4-way reversing valve closes.

When Tr≥Ts+2℃,the running mode is the same to the cooling operation;

When Ts-1℃< Tr < Ts+2℃, compressor and outdoor fan motor run continuously. And indoor fan motor runs at low fan speed

When 15℃< Tr < Ts-1℃, compressor and outdoor fan motor are working according to 3 minutes working alternating with 9 minutes stopping. Indoor fan motor runs at low fan speed when compressor is running, and it runs at breeze level for 30 seconds later the turn-off of compressor. 30 seconds later, fan motor will turn off.

When Tr≤15℃, indoor and outdoor fan motor will stop running, louver blades (vertical direction) can’t be controlled.

2.3.4. Heating (not available for cooling-only type air conditioner)

Temperature control range: 16℃-32℃; Original value: 24℃;

Temperature control precision: ±1℃;

Characters on control:

4-way reversing valve opens.

When Tr≤Ts-1℃, compressor, 4-way reversing valve and outdoor fan motor all open.

When Tr≥Ts+1℃, compressor and outdoor fan motor both close; Indoor fan motor is running at low

level.

Manual: Users can select the fan speed of high, medium or low level as needed.

Auto: When Tr< Ts-2℃, high speed; When Tr≥Ts-2℃,medium speed;

2.3.5 Fan sweep

In this mode, compressor, outdoor fan motor all open.

Indoor fan motor can be set at high, medium, low level as needed.

Manual (vertical direction): Set the blades position as needed.

## 2.4 Protection function

2.4.1 Delay-starting protection for the compressor

Compress will restart working 3 minutes later the turn-off of compressor or power-off to keep the pressure balance of the cooling system.

2.4.2 Freeze-prevention: To prevent indoor heat exchanger freezing in cool and dry operation.

When Trc≤3℃, the unit will enter freeze-prevention operation. If indoor fan speed is at low or breeze level, it will turn to medium speed automatically; if indoor fan speed is at medium speed, it will turn to high speed;, The air conditioner will exit Freeze-prevention operation when Trc>10℃, indoor fan motor runs at the set fan speed. Compressor will stop running when it runs at least 10 minutes and Trc≤0℃. If the off-time of compressor is for more than 6 minutes or Trc≥10℃, and the compressor stops running for more than 3 minutes. Compressor and outdoor fan motor will restart working. The air conditioner will exit Freeze-prevention operation, and indoor fan motor is running at the set speed.

2.4.3 Testing codes:

Code 1 is to set test run (Not effective for “SMART” mode and “DEHUMIDIFICATION” mode. After entering testing run, no matter what is the set temperature or indoor temperature, the unit will run as the set cooling or heating mode and will also not detect stopping condition. The max. running time is 60 minutes.)

Code 2 is to set fast testing.

Code 3 is to set auto-diagnosis.

Code 4 is to cancel the above setting.

There only can be one setting each time in the tests above.

## 2.5 Other functions

2.5.1 Auto-diagnosis

The Auto-diagnosis functions are in the following steps:

Buzzer beeps 1s →no output 0.5s→running indicator lights 0.5s→pause indicator lights 0.5s→timer indicator lights 0.5s→air refresh indicator lights 0.5s →running compressor on 0.5s→outdoor fan motor 0.5s→4-way reversing valve 0.5s→AUH 0.5s→indoor fan motor high level 0.5s→indoor fan motor medium level 0.5s→indoor fan motor low level 0.5s→air refresh indicator lights 0.5s→FLAP-a 0.5s→FLAP-b 0.5s→FLAP-c 0.5s→FLAP-d 0.5s→no output 0.5s→all output 1s.

2.5.2 Time reducing:

The CPU runs as 60 times as the former speed. (There is no timer reducing function within 1 minute)

2.5.3 Display function:

The central display screen does not display symbols if air conditioner is in off status, but Timer indicator lights when in Timer mode. In the checking and setting conditions, the screen will also display the corresponding state of the unit.

Press the DIAPLAY button,the screen will turn on or turn off immediately;

Press the SLEEP button to enter sleep function,the screen will turn off after 30s,when press the button again,the screen will turn on immediately.

2.5.4 Air refresh function:

Press air refresh button when the unit is in off status, the unit will switch on. Indoor fan motor runs at the set fan speed, air refresh outputs. Press this button again, air refresh function is cancelled and the unit will turn back to the original mode. Press air refresh button if the unit is running, air refresh indicator will light and air refresh output. Press this button again, air refresh function is cancelled and the unit will turn back to the original running mode.

2.5.5 Quiet Operation

Press “QUIET” button when air conditioner is “FAN SWEEP” status, the indoor fan will run at low level.

Press “AIR REFRESH” button when air conditioner is in off status and set fan speed as quite mode, the indoor fan will run at low level.

In other status, the indoor fan runs at low level.

2.5.6Restoration function (optional)

To install E2PROM, users do not have to program first and then assemble. As long as installing E2PROM, the unit will have the restoration function after electricity comes again.

2.5.7 Restoration (optional)

Mode

Fan speed

On/Off status

Dew-prevention symbol

Fan sweep symbol

Sleep symbol

Quiet symbol

Air refresh symbol

Set temperature

Louver position

2.5.8 The second function button

The second function for “AIR REFRESH” button:

Press “AIR REFRESH” button and hold on, and finish the test condition after 5 seconds. When entering this mode, the original value is 00 for each entry. The second function is only effective for temperature control button, on/off button, and air refresh button. Other buttons are not effective for the second function.

The second function for “AUH” button:

Press “AUH” button and hold on for 5 seconds, the unit will enter dew-prevention function. At the same time, the unit gives a buzz sound. This button is only effective in Cooling and Dehumidification mode. Users can set or cancel this function by pressing this button. (Y2 model gives tacit consent automatically to start dew-prevention function.)

2.5.9 Demonstration Mode: (Blank unit)

When electrified, the unit runs at medium level if the unit has not received the signal from remote controller.

Pause indicator lights 1s→running indicator lights 1s→timer indicator lights 1s→air refresh indicator lights 1s →Pause indicator lights 1s→……; The display screen displays every 11,22,33,44,55,66,77,88,99,00 1s circularly.

After receiving the signal from the remote controller, the unit will operate by the signal.

During the courts of demonstration, all signals of outdoor unit are ineffective.

2.5.10  UVC function（optional）

Press the UVC bottom on remote controller to start or stop UVC sterilize function.

Note：

1.This appliance contains a UVC lamp.

2.Unintended use of the appliance or damage to the housing may result in the escape of dangerous UVC radiation. UVC radiation may, even in small doses, cause harm to the eyes and skin.

3.Appliances that are obviously damaged must not be operated. Prior to cleaning or other maintenance, the appliance must be disconnected from the supply mains.

3. Exploded view

## 3.1 Exploded view for indoor unit

| NO | Materails Description | NO | Materails Description |
| --- | --- | --- | --- |
| 1 | Front panel subassembly | 21 | Negative ion generator（optional） |
| 2 | Front panel | 22 | electric heating tube（optional） |
| 3 | Air filter | 23 | Positive and negative ion generate （optional） |
| 4 | Medium frame subassembly | 24 | Sensor bracket |
| 5 | Screw cover | 25 | Electric control board |
| 6 | Evaporator subassembly | 26 | Spring |
| 7 | pressure plate | 27 | Display box |
| 8 | Bearing | 28 | Display P.C.B assembly |
| 9 | Bottom frame subassembly | 29 | WIFI subassembly（optional） |
| 10 | Stepping motor（optional） | 30 | Electric control box board(metal) （optional） |
| 11 | Blade | 31 | Cover of electirc control box |
| 12 | Wall-Mounting frame | 32 | Transformer |
| 13 | Pipe pressure plate | 33 | Terminal board |
| 14 | Drainage pipe subassembly | 34 | Wire pressure plate |
| 15 | Stepping motor | 35 | Electirc control box |
| 16 | Crossflow fan | 36 | P.C.B assembly |
| 17 | Motor Bracket (bottom) | 37 | Electric control box(metal shell) （optional） |
| 18 | Fan motor | 38 | Power line |
|  |  | 39 | Room temperature sensor |
|  |  | 40 | Pipe temperature sensor |
| 19 | Motor Bracket（top) | 41 | Negative ion generator（optional） |
| 20 | Motor cover |  |  |

NOTE:Actual product may be different from above graphics,please refer to actual products.

## 4.2 Exploded view for outdoor unit

| NO | Materails Description |
| --- | --- |
| 1 | Fluorine charing pipe |
| 2 | front plate subassembly |
| 3 | propeller fan |
| 4 | fan motor |
| 5 | motor bracket subassembly |
| 6 | bottom plate subassembly |
| 7 | Metal support |
| 8 | partition board |
| 9 | Top cover assembly |
| 10 | condenser subassembly |
| 11 | rear net cover |
| 12 | capillary subassembly |
| 13 | electric cover subassembly |
| 14 | Valve mounting plate |
| 15 | Lateral plate assembly |
| 16 | cut-off valve |
| 17 | four-way valve subassembly |
| 18 | compressor |
| 19 | membrane capacitor(compressor) |
| 20 | membrane capacitor(fan motor) |
| 21 | capacitor clip |
| 22 | electric control installion plate |
| 23 | connection terminal block |
| 24 | lead assembly |
| 25 | electric control assembly |

NOTE:Actual product may be different from above graphics,please refer to actual products.

# 5. Refrigerant Flow Diagram

Thermal insulating of refrigerant pipeline

To prevent heat loss and condensed water from dropping on the floor, the wide and narrow tube of air conditioner should be wrapped with thermal insulating materials. For using capillary tube, and the tubes are in low temperature, the thickness of thermal insulating materials shall be more than 8mm.

# 6. Circuit Diagram

## 6.1 Electrical wiring diagram for indoor unit

To avoid electrical shock hazard, be sure to disconnect power before checking, servicing and/or cleaning any electrical parts.

12K、18K：

## 24K：

## 6.2 Electrical wiring diagram for outdoor unit

To avoid electrical shock hazard, be sure to disconnect power before checking, servicing and/or cleaning any electrical parts.

12K、18K：

24K：

# 7 Trouble shooting

7.1 Check before troubleshooting

7.1.1 Check power line

To check whether the power line is connected correctly to the terminal No 1 which is on the terminal block of the indoor unit

12K、18K：                                     24K：

7.1.2 Check unit wiring

To check whether the inter-unit wires are connected correctly.

7.1.3 Check power supply

To check whether the power supply is in the specified range (220-240V).

7.1.4 Check connector and lead wire of indoor and outdoor units.

To check whether the insulating cover of the lead wire is damaged.

To check whether the lead wire and the connector are connected well

To check wires.

## 7.2 The air conditioner does not work

7.2.1 Leakage protector is open or fuse is burnt.

A. Setting leakage protector to “ON”, it opens immediately (can not reset).

There is possibility of ground fault.

Check insulation resistance (The insulation resistance shall be more than 2MΩ).

- Leakage protector is OFF.

- The fuse is open in several minutes after turning air conditioner on.

7.2.2 The indoor and outdoor units do not work.

7.2.3 Only outdoor unit does not work.

7.2.4 Indoor unit does not work.

## 7.3 Some parts of the air conditioner do not work

7.3.1 Only indoor fan does not work.

7.3.2 Only louver motor does not run.

7.3.3 Only outdoor fan motor dos not run.

7.3.4 Compressor does not run.

## 7.4 Air conditioner operates, but abnormalities are observed

7.4.1 Poor shifting between cooling and heating. (Inapplicable for cooling-only type)

7.4.2 Poor cooling or heating phenomena.

NOTE: “          ”Inapplicable for cooling-only type.

7.4.3 Over cooling or heating.

## 7.5 Sensor is defective (Check reference 3.4.9)

# 8. Checking Electrical Components

8.1 Measure insulation resistance

The insulation is in good condition if the resistance exceeds 2 MΩ.

8.1.1 Power supply wires

Clamp the ground pins of the power plug with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on either of the power wires. (Fig. 1)

Then measure the resistance between the

ground wire and the other power wire. (Fig. 1)

8.1.2 Indoor unit

Clamp an aluminum plate fin or copper tube with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on each terminal screw on the terminal plate. (Fig. 2)

Note that the ground line terminal should be skipped for the check.

8.1.3 Outdoor unit

Clamp a metallic part of the unit with the lead clip of the insulation resistance tester and measure the resistance by placing a probe on each terminal screw where power supply lines are connected on the terminal plate. (Fig. 2)

8.1.4 Measurement of Insulation Resistance for Electrical Parts

Disconnect the lead wires of the desired electric part from terminal plate, capacitor, etc.

Similarly disconnect the connector. Then measure the insulation resistance. (Fig. 3 and 4)

8.2 Checking continuity of fuse on PCB Ass'y

Remove the PCB ass’ y from the electrical component box. Then pull out the fuse from the PCB ass’ y. (Fig. 5)

Check for continuity using a multimeter as shown in Fig. 6

8.3 Checking motor capacitor

Remove the lead wires from the capacitor terminals, and then place a probe on the capacitor terminals as shown in Fig. 7. Observe the deflection of the pointer setting the resistance measuring range of the multimeter to the maximum value.

The capacitor is “good” if the pointer bounces to a great extent and then gradually returns to its original position.

The range of deflection and deflection time differ according to the capacity of the capacitor.

# 9.ERROR CODES

| Error code | Troubleshooting | Solution |
| --- | --- | --- |
| F1 | Indoor ambient temp sensor short\open | Measuring the sensor resistance value ,if the resistance is infinity or zero,it should be replaced by a new one. |
| F2 | Indoor mid-pipe temp sensor short\open |  |
| F3 | Outdoor mid-pipe temp sensor short\open |  |
| F4 | Air conditioner indoor fan malfunction | Check the connection of the fan and the Indoor main board，including the fan line and feedback line. |
| F5 | Indoor main board and display board communication malfunction | Check the connection of the Indoor main board and display board. |

If the problem is not solved,please contact the professional person or supplier.

# Text boxes

###### Warning

###### Warning

High-voltage will result in electric shock or death.

Always cut off the power before checking and maintaining.

Warning:

Disconnect unit wires from terminal block of outdoor unit. And measure insulation resistance of outdoor unit.

Poor insulation performance

No

Measure the insulation resistance of the electric parts of outdoor unit.

Disconnect unit wires from terminal block of indoor unit. Unplug the unit and measure the insulation resistance of indoor unit.

No

Measure the insulation resistance of the electric parts of outdoor unit.

Poor insulation performance

Check the rated power of fuse.

Check the resistance of indoor fan motor coil.

Check the resistance of transformer coil.

Replace it with a proper one

Replace indoor fan motor.

Replace transformer.

No

No

No

Yes

Yes

Check power supply.

Check if something residue cover on transmitting part of the remote controller.

1. Power failure

2. Check the breaker.

Clean it.

Check if infrared receiver on indoor unit is dirt.

Clean it.

Check fuse on indoor PCB Ass’ y.

Check the resistance of indoor fan motor coil.

Parts of indoor PCB Ass’ y or switches are defective.

Measure the resistance of power transformer.

No

No

No

No

Yes

Yes

Yes

Yes

Measure the resistance of compressor coil.

No

Yes

Check the set temperature

1. The set temperature is too high in cooling.

2. The set temperature is too low in heating.

Adjust the set temperature

Measure the voltage between terminal No.1 and No.2 on the terminal block (220-240V)

PCB Ass’ y of indoor unit is defective.

Outdoor unit is defective.

Ok

No voltage indication

Indoor PCB Ass’ y is defective.

Check the fan rotation

Check if foreign matter is in the fan cover.

Check if fan motor is broken or foreign matter in bearing.

Measure the resistance of motor coil.

Check the capacitor of fan motor.

Ok

Ok

Not rotate

Measure the resistance of the louver motor coil.

Replace louver motor.

To check whether the butt plugs of louver motor are connected well.

Integrate circuit ‘ULN2003’ is defective.

Plug well.

Ok

Ok

No

No

Check the fan rotation

Check if foreign matter is in the fan cover.

Check if fan motor is broken or foreign matter in bearing.

Measure the resistance of motor coil.

Check the capacitor of the fan motor.

Ok

Ok

Not rotate

Check compressor capacitor.

Measure the resistance of compressor coil.

Measure the resistance of power relay coil.

Measure if power supply voltage is too low.

Overload protector activates.

The temperature of compressor is too high.

Refrigerant is not enough.

Fill it.

Rotor may be blocked.

Yes

No

Remote controller may be defective.

Measure the resistance of 4-way reversing valve coil.

Cooling → Heating

Measure the voltage between terminal No.5 and No.2 on the outdoor terminal block (220-240V) (Adding 6 W loading in measuring)

Four-way reversing valve is defective.

PCB Ass’ y of indoor unit is defective.

OK

No voltage indication

Poor cooling (heating) performance

Is the temperature set properly?

Change the set temperature.

The heating (cooling) load is too large.

Reduce heat (cool) source or change the air conditioner with large power.

Refrigerant flow is not enough

Refrigerant is not enough.

Capillary tube is blocked.

Compressor is in error.

Service valve is not open completely.

Air circulating capacity is not enough.

The air filter is blocked.

4-way reversing valve fails.

Replace it

Fan running speed is at “low”.

Change it to “high’ or “medium”.

Connection between indoor and outdoor units is in poor thermal-insulated.

Wide and narrow tubes are thermal-insulated separately.

Cooling air -flow

4-way reversing valve is defective.

Cooling airflow protector is no use.

The pause indicator is on.

Replace the electric controller of indoor unit.

Temperature sensor of indoor coil is defective.

Replace the sensor.

No

Yes

Filling it.

Replace it.

Replace it.

Open it completely

Clean it.

Replace it

Check the set temperature.

Refer to electric wiring diagram.

If the probe can’t enter the poles because the hole is too narrow then use a probe with a thinner pin.

Note: